{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":142,"n_cols":11,"rows_kept":142,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYSQ-TY1"]
[]
[]
[]
[]
["","","","","","RXYSQ4T7Y1B","RXYSQ5T7Y1B","RXYSQ6T7Y1B","RXYSQ8TMY1B","RXYSQ10TMY1B","RXYSQ12TMY1B"]
["Sound pressure level","Cooling","","Nom.","dBA","50 (5)","51 (5)","","55.0 (8)","55.0 (8)","57.0 (8)"]
["Standard Accessories","Installation manual","","","","Installation manual","Installation manual","Installation manual","1","1","1"]
["","Operation manual","","","","Operation manual","Operation manual","Operation manual","1","1","1"]
["","Connection pipes","","","","Connection pipes","Connection pipes","Connection pipes","1","1","1"]
["SEER recommended combination 2","","","","","","","","6.0","6.3","6.3"]
["Capacity range","HP","","","","4","5","6","8","10","12"]
["Operation range","Cooling","","Max.","°CDB","46","46","","52.0","52.0","52.0"]
["","","","Min.","°CDB","-5","-5","","-5.0","-5.0","-5.0"]
["","Heating","","Min.","°CWB","-20","-20","","-20.0","-20.0","-20.0"]
["","","","Max.","°CWB","15.5","15.5","","15.5","15.5","15.5"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)","64 (6)","64 (6)","64 (6)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","","","","16.5","20.6","24.7"]
["","","","EERd","","","","","4.2","4.3","4.3"]
["","D Condition (20°C - 27/19)","","Pdc","kW","","","","6.4","7.1","7.3"]
["","","","EERd","","","","","13.7","12.2","13.6"]
["","A Condition (35°C - 27/19)","","EERd","","","","","2.6","2.8","2.7"]
["","","","Pdc","kW","","","","22.4","28.0","33.5"]
["","C Condition (25°C - 27/19)","","EERd","","","","","7.7","7.7","7.9"]
["","","","Pdc","kW","","","","10.6","13.3","15.9"]
["SCOP","","","","","","","","4.2","4.1","4.3"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","104","104","","144","175","180"]
["Refrigerant","Charge","","","TCO2Eq","7.5","7.5"]
["","GWP","","","","2,087.5","2,087.5","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","3.6","3.6","","5.5","7.0","8.0"]
["","Type","","","","R-410A","R-410A","","R-410A","R-410A","R-410A"]
["Space cooling recommended combination 2","C Condition (25°C - 27/19)","","Pdc","kW","","","","10.6","13.3","15.9"]
["","","","EERd","","","","","7.5","7.7","7.7"]
["","A Condition (35°C - 27/19)","","EERd","","","","","2.3","2.8","2.5"]
["","","","Pdc","kW","","","","22.4","28.0","33.5"]
["","D Condition (20°C - 27/19)","","EERd","","","","","13.4","12.4","13.5"]
["","","","Pdc","kW","","","","6.4","7.3","7.3"]
["","B Condition (30°C - 27/19)","","EERd","","","","","4.2","4.4","4.2"]
["","","","Pdc","kW","","","","16.5","20.6","24.7"]
["Recommended combination 2","","","","","","","","4 x FXSQ50A2VEB","4 x FXSQ63A2VEB","6 x FXSQ50A2VEB"]
["SCOP recommended combination 2","","","","","","","","4.2","4.1","4.3"]
["Power input - 50Hz","Cooling","Nom.","Eurovent","kW","3.03 (1)","3.73 (1)"]
["","Heating","Nom.","6°CWB","kW","2.68 (2)","3.27 (2)","","5.82 (5)","6.60 (5)","8.19 (5)"]
["Indoor index connection","Min.","","","","50","62.5","","100.0","125.0","150.0"]
["","Max.","","","","130","162.5","","260.0","325.0","390.0"]
["Cooling capacity","Nom.","","Eurovent","kW","12.1 (1)","14.0 (1)"]
["COP at nom. capacity","6°CWB","","","kW/kW","4.52 (2)","4.28 (2)","","3.85","4.24","4.09"]
["Recommended combination","","","","","","","","4 x FXMQ50P7VEB","4 x FXMQ63P7VEB","6 x FXMQ50P7VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","","","","2.4","2.2","2.2"]
["","","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tol (temperature operating limit)","°C","","","","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","","","","5.8","6.4","6.6"]
["","","","COPd (declared COP)","","","","","7.8","6.3","6.7"]
["","B Condition (2°C)","","COPd (declared COP)","","","","","4.0","4.1","4.3"]
["","","","Pdh (declared heating cap)","kW","","","","8.0","10.6","12.7"]
["","C Condition (7°C)","","COPd (declared COP)","","","","","5.9","5.9","6.3"]
["","","","Pdh (declared heating cap)","kW","","","","5.0","6.8","8.1"]
["","A Condition (-7°C)","","COPd (declared COP)","","","","","2.6","2.4","2.4"]
["","","","Pdh (declared heating cap)","kW","","","","13.2","17.4","20.8"]
["","TBivalent","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","Tbiv (bivalent temperature)","°C","","","","-10","-10","-10"]
["","","","COPd (declared COP)","","","","","2.4","2.2","2.2"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","","9.52","9.52","12.7"]
["","","","Type","","Flare connection","Flare connection","","Braze connection","Braze connection","Braze connection"]
["","Total piping length","System","Actual","m","","","","300 (9)","300 (9)","300 (9)"]
["","Gas","","OD","mm","15.9","15.9","","19.1","22.2","25.4"]
["","","","Type","","Flare connection","Flare connection","","Braze connection","Braze connection","Braze connection"]
["","Heat insulation","","","","Both liquid and gas pipes","Both liquid and gas pipes"]
["SEER","","","","","","","","6.3","6.3","6.5"]
["Space heating (Average climate) recommended combination 2","B Condition (2°C)","","Pdh (declared heating cap)","kW","","","","8.0","10.6","12.7"]
["","","","COPd (declared COP)","","","","","4.0","4.1","4.2"]
["","C Condition (7°C)","","Pdh (declared heating cap)","kW","","","","5.2","6.8","8.1"]
["","","","COPd (declared COP)","","","","","5.8","5.9","6.2"]
["","A Condition (-7°C)","","COPd (declared COP)","","","","","2.6","2.4","2.3"]
["","","","Pdh (declared heating cap)","kW","","","","13.2","17.4","20.8"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","","","","5.7","6.4","6.5"]
["","","","COPd (declared COP)","","","","","7.7","6.3","6.6"]
["","TBivalent","","Pdh (declared heating cap)","kW","","","","14.9","19.6","23.5"]
["","","","COPd (declared COP)","","","","","2.3","2.2","2.2"]
["","","","Tbiv (bivalent temperature)","°C","","","","-10.0","-10.0","-10.0"]
["Sound power level","Cooling","","Nom.","dBA","68 (4)","69 (4)","","73.0 (7)","74.0 (7)","76.0 (7)"]
["Dimensions","Unit","","Width","mm","900","900","","940","940","940"]
["","","","Depth","mm","320","320","","320","460","460"]
["","","","Height","mm","1,345","1,345","","1,430","1,615","1,615"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","106","106"]
["Heating capacity","Nom.","","6°CWB","kW","12.1 (2)","14.0 (2)","","22.4 (5)","28.0 (5)","33.5 (5)"]
["Power supply","Phase","","","","3N~","3N~","","3N~","3N~","3N~"]
["","Name","","","","Y1","Y1","","Y1","Y1","Y1"]
["","Frequency","","","Hz","50","50","","50","50","50"]
["","Voltage","","","V","380-415","380-415","","380-415","380-415","380-415"]
["Notes","","","","","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used.","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used.","(2) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series. Eurovent 2015 tolerances are used.","(2) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included","(2) - Cooling: T1: indoor temp. 26,7°CDB, 19,4°CWB, outdoor temp. 35°CB, AHRI 1230:2010, power input indoor units (duct type) included"]
["","","","","","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(3) - Sound power level is an absolute value that a sound source generates.","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included","(3) - Cooling: T3: indoor temp. 29,0°CDB, 19,0°CWB, outdoor temp. 46°CB, ISO15042:2011, power input indoor units (duct type) included"]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included","(4) - Cooling: T2: indoor temp. 26,6°CDB, 19,4°CWB, outdoor temp. 48°CB, AHRI 1230:2010, power input indoor units (duct type) included"]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(5) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(6) - Sound values are measured in a semi-anechoic room.","(6) - Sound values are measured in a semi-anechoic room.","(6) - TOCA means the total value of each OC set.","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%).","(6) - Actual number of units depends on the indoor unit type (VRV DX indoor, RA DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤130%)."]
["","","","","","(7) - For detailed contents of standard accessories, see installation/operation manual","(7) - For detailed contents of standard accessories, see installation/operation manual","","(7) - Sound power level is an absolute value that a sound source generates.","(7) - Sound power level is an absolute value that a sound source generates.","(7) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(8) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(9) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","","(9) - Refer to refrigerant pipe selection or installation manual","(9) - Refer to refrigerant pipe selection or installation manual","(9) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(10) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(11) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(12) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(13) - FLA: nominal running current fan","(13) - FLA: nominal running current fan","","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(13) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(14) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(15) - Maximum allowable voltage range variation between phases is 2%.","(15) - Maximum allowable voltage range variation between phases is 2%.","","(15) - TOCA means the total value of each OC set.","(15) - TOCA means the total value of each OC set.","(15) - TOCA means the total value of each OC set."]
["","","","","","(16) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(16) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","","(16) - FLA means the nominal running current of the fan","(16) - FLA means the nominal running current of the fan","(16) - FLA means the nominal running current of the fan"]
["","","","","","(17) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(17) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","","(17) - Maximum allowable voltage range variation between phases is 2%.","(17) - Maximum allowable voltage range variation between phases is 2%.","(17) - Maximum allowable voltage range variation between phases is 2%."]
["Cooling capacity","Nom.","","Eurovent","kW","","","15.5 (1)"]
["Heating capacity","Nom.","","6°CWB","kW","","","15.5 (2)"]
["COP at nom. capacity","6°CWB","","","KW/KW","","","3.9"]
["Indoor index connection","Min.","","","","","","70"]
["","Max.","","","","","","182"]
["Dimensions","Unit","","Height","mm","","","1345"]
["","","","Width","mm","","","900"]
["","","","Depth","mm","","","320"]
["Weight","Unit","","","kg","","","104"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","","","106"]
["Compressor","Type","","","","","","Hermetically sealed swing compressor"]
["Operation range","Cooling","","Min.","°CDB","","","-5"]
["","","","Max.","°CDB","","","46"]
["","Heating","","Min.","°CWB","","","-20"]
["","","","Max.","°CWB","","","15.5"]
["Sound power level","Cooling","","Nom.","dBA","","","70 (4)"]
["Sound pressure level","Cooling","","Nom.","dBA","","","51 (5)"]
["Refrigerant","Type","","","","","","R-410A"]
["","GWP","","","","","","2087.5"]
["","Charge","","","tCO2Eq","","","7.5"]
["","Charge","","","kg","","","3.6"]
["Piping connections","Liquid","","OD","mm","","","9.52"]
["","Gas","","OD","mm","","","19.1"]
["Power supply","Name","","","","","","Y1"]
["","Phase","","","","","","3N~"]
["","Frequency","","","Hz","","","50"]
["","Voltage","","","V","","","380-415"]
["Notes","","","","","","","","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(18) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","","","","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control).","(19) - The automatic ESEER value corresponds with normal VRV IV-S heat pump operation, including the advanced energy saving functionality (variable refrigerant temperature control)."]
["","","","","","","","","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality.","(20) - The standard ESEER value corresponds with normal VRV IV-S heat pump operation, not taking into account the advanced energy saving functionality."]
["","","","","","","","","(21) - Sound values are measured in a semi-anechoic room.","(21) - Sound values are measured in a semi-anechoic room.","(21) - Sound values are measured in a semi-anechoic room."]
["","","","","","","","","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","","","","(23) - Ssc: Short-circuit power","(23) - Ssc: Short-circuit power","(23) - Ssc: Short-circuit power"]
["","","","","","","","","(24) - For detailed contents of standard accessories, see installation/operation manual","(24) - For detailed contents of standard accessories, see installation/operation manual","(24) - For detailed contents of standard accessories, see installation/operation manual"]